## Properties
Tdb1 | 80 | °F | Tdb2 | 55 | °F
Twb1 | 67 | °F | Twb2 | 54 | °F
Elevation | 650 | ft.
AtmPress | 14.3541 | psia
APinHg | 29.2252 | in Hg
HRatio1 | 0.011514 | lbw/lba | HRatio2 | 0.0088458 | lbw/lba
| 80.5967 | Grains |  | 61.9206 | Grains
RelHum1 | 51.4213 | % | RelHum2 | 94.0129 | %
SpHt1 | 0.24511 | Btu/lb-°F | SpHt2 | 0.24393 | Btu/lb-°F
Enal1 | 31.8251 | Btu/lb | Enal2 | 22.8014 | Btu/lb
SpVol1 | 14.1867 | cu.ft./lb | SpVol2 | 13.4725 | cu.ft./lb
DewPt1 | 60.5462 | °F | DewPt2 | 53.3735 | °F
lbpCuFt | 0.00081159 | lbw/ft3 | lbpCuFt | 0.00065658 | lbw/ft3
Note 1: In these programs, required input values are in yellow cells. Output values are in blue or green.
The Psychrometric Chart

## Mixing
Qair1 | 5000 | cfm |  | Qair2 | 1000 | cfm
QSair1 | 4699.241 | scfm |  | QSair2 | 989.6693 | scfm
| Stream 1 |  |  |  | Stream 2
mflow1 | 21146.5845 | lb/hr |  | mflow2 | 4453.5118 | lb/hr
|  |  | Stream 3 | (mixed)
|  | mflow3 | 25600.0964 | lb/hr
|  | Qair3 | 5999.8303 | cfm
|  | Tdb3 | 75.6509 | °F
|  | HRatio3 | 0.01105 | lbw/lba
|  |  | 77.3477 | Grains
|  | Twb3 | 65.0509 | °F
|  | RelHum3 | 57.2832 | %
|  | SpHt3 | 0.24491 | Btu/lb-°F
|  | Enal3 | 30.2511 | Btu/lb
|  | SpVol3 | 14.062 | cu.ft./lb
|  | DewPt3 | 59.4145 | °F
Mixing - This Worksheet computes the resulting properties of air (stream 3) when streams 1 and 2 are mixed. Flow rates are entered below but properties for streams 1 and 2 are entered on the "Properties" Worksheet.
Note: Input values (Qair1 and Qair2) are in cubic feet per minute. For additional information purposes, these values are corrected to air at standard conditions of ρ=0.075 lb/cu.ft. (QSair1 and QSair2).
Stream 2 @ Qair2(cfm), Tdb2(°F), & Twb2(°F)
Stream 1 @ Qair1(cfm), Tdb1(°F), & Twb1(°F)
Stream 3 @ Qair3(cfm), Tdb3(°F), & Twb3(°F)
1
2
3

## Heat Rec'ry
HRU | Effectiveness |  |  | Room Air
SenEff | 70 | % |  | TdbRm | 75
LatEff | 65 | % |  | TwbRm | 63 | °F
| Outdoor |  |  | Outdoor Air |  | °F
QairOut | 10000 | cfm |  | TdbOut | 96
QSairOut | 9088.0288 | scfm |  | TwbOut | 75 | °F
mflowOut | 40896.1298 | lb/hr |  | Elev. | 600 | ft.
SupFankW | 0 | kW |  |  |  | HRU Outlet |  |  |  | OALoads
ExFankW | 0 | kW | Capacities | MBtu/h | Tons |  | Temps. |  |  | MBtu/h | Tons
| Exhaust | (not req'd) | qTotalHru | 278.1604 | 23.18 | TdbHru | 81.3 | °F | Total | 411.1546 | 34.2629
QairEx | 2000 | cfm | qSenHru | 148.0959 | 12.3413 | TwbHru | 67.3 | °F | Sensible | 211.5656 | 17.6305
QSairEx | 1979.3386 | scfm | SHRHru | 0.53241
| Room Air |  |  | Outdoor Air |  |  | HRU Outlet
HRatioRm | 0.0098305 | lbw/lba | HRatioOut | 0.01429 | lbw/lba | HRatioHru | 0.011391 | lbw/lba
| 68.8136 | Grains |  | 100.0324 | Grains |  | 79.7402 | Grains
RelHumRm | 51.9306 | % | RelHumOut | 38.3037 | % | RelHumHru | 48.9619 | %
SpHtRm | 0.24436 | Btu/lb-°F | SpHtOut | 0.24634 | Btu/lb-°F | SpHtHru | 0.24506 | Btu/lb-°F
EnalRm | 28.7575 | Btu/lb | EnalOut | 38.8112 | Btu/lb | EnalHru | 32.0095 | Btu/lb
SpVolRm | 14.0179 | cu.ft./lb | SpVolOut | 14.6713 | cu.ft./lb | SpVolHru | 14.2181 | cu.ft./lb
DewPtRm | 56.2236 | °F | DewPtOut | 66.563 | °F | DewPtHru | 60.252 | °F
HRU
Room Air
Outdoor Air
HRU Outlet Air to room or HVAC Unit
Exhaust Air
This Worksheet computes the properties of air leaving Heat Recovery Units (HRU) used to adsorb or remove heat (and in some units moisture) from room air that is being exhausted. The heat and moisture are transfered to or from the fresh outdoor air make-up air. The capacity of the HRU is also computed. The effects of the HRU supply fan heat are considered.
D
t(o)
t(r)
t(hru)
Summer
D
D
Winter
t(hru)
t(o)

## Htg Coil
Inlet | Conditions |  | Outlet | Conditions |  | Outlet | Conditions
|  |  | Without | Humidification |  | With | Humidification*
QairHin | 2000 | cfm |  |  |  | TdbOutAir | 20 | °F
qFurn | 75 | MBtu/h |  |  |  | TwbOutAir | 15 | °F
QSairHin | 1983.0098 | scfm |  |  |  | OAVentInfil | 20 | % of supply
mflowHin | 8923.5439 | lb/hr | TdbHout | 102.585 | °F | HRatioOA | 0.00073535 | lbw/lba
|  |  | TwbHout | 68.185 | °F |  | 5.1475 | Grains
TdbHin | 68 | °F |  |  |  | RelHumOA | 32.2089 | %
TwbHin | 56 | °F |  |  |  | SpHtOA | 0.24033 | Btu/lb-°F
ElevH | 0 | ft. | HRatioHout | 0.0067944 | lbw/lba | EnalOA | 5.5867 | Btu/lb
APpsia | 14.696 | psia |  | 47.5611 | Grains | SpVolOA | 12.1065 | cu.ft./lb
APHg | 29.9213 | in Hg | RelHumHout | 15.6302 | % | DewPtOA | -6.8363 | °F
|  |  | SpHtHout | 0.24302 | Btu/lb-°F
|  |  | EnalHout | 32.1388 | Btu/lb | FluidType | Sat Steam
HRatioHin | 0.0067944 | lbw/lba | SpVolHout | 14.329 | cu.ft./lb | FluidTemp | 212 | °F
| 47.5611 | Grains | DewPtHout | 46.9974 | °F | EnalFluid | 1150.04 | Btu/lb
RelHumHin | 46.8151 | % |  |  |  | mfluid | 10.8137 | lb/hr
SpHtHin | 0.24302 | Btu/lb-°F |  |  |  | qHumid | 0.47031 | MBtu/h
EnalHin | 23.734 | Btu/lb |  |  |  | TdbHumOut | 102.8019 | °F
SpVolHin | 13.4476 | cu.ft./lb |  |  |  | qNet | 75.4703 | MBtu/h
DewPtHin | 46.9974 | °F
t(in)
Water
Steam
t(out)
t(in)
t(out)
*Assumption: Sufficient moisture is added in the form of water or saturated steam to replace the moisture lost via the exhaust air, which is replace with dryer outdoor air.

## Clg-Coil
Inlet Air | Conditions |  | Fan Heat | Neglected |  | Fan Heat | Included
QairIn | 10000 | cfm |  |  |  | TotalPress | 2 | In. of Water
TC | 120 | MBtu/h |  |  |  | FanEff | 65 | %
SC | 100 | MBtu/h |  |  |  | MotorEff | 82 | %
QSairIn | 9742.8044 | scfm |  |  |  | BHP | 4.7209 | hp
SHR | 0.83333 |  |  |  |  | qFan | 14.6521
TdbIn | 75 | °F | mflowIn | 43842.6198 | lb/hr | qTotNet | 105.3479 | MBtu/h
TwbIn | 63 | °F | QairOut | 9818.6138 | cfm | qSenNet | 85.3479 | MBtu/h
ElevIn | 0 | ft. | QSairOut | 9742.8044 | scfm | SHRNet | 0.81015
AtmPressIn | 14.696 | psia
APinHgIn | 29.9213 | in Hg | TdbOut | 65.661 | °F | TdbNet | 67.0294 | °F
|  |  | TwbOut | 59.061 | °F | TwbNet | 59.5294 | °F
HRatioIn | 0.009533 | lbw/lba | HRatioOut | 0.0091012 | lbw/lba | HRatioNet | 0.0091012 | lbw/lba
| 66.7311 | Grains |  | 63.7086 | Grains |  | 63.7086 | Grains
RelHumIn | 51.5829 | % | RelHumOut | 68.1187 | % | RelHumNet | 64.7935 | %
SpHtIn | 0.24423 | Btu/lb-°F | SpHtOut | 0.24404 | Btu/lb-°F | SpHtNet | 0.24404 | Btu/lb-°F
EnalIn | 28.432 | Btu/lb | EnalOut | 25.6804 | Btu/lb | EnalNet | 26.0143 | Btu/lb
SpVolIn | 13.6853 | cu.ft./lb | SpVolOut | 13.4371 | cu.ft./lb | SpVolNet | 13.4721 | cu.ft./lb
DewPtIn | 56.0385 | °F | DewPtOut | 54.7836 | °F | DewPtNet | 54.7836 | °F
In
Out
Fan Heat Included
Fan Heat Neglected
Net

## Clg Coil-BP
By-Pass (BP) | Factor
Method
QairRet | 4000 | cfm | mflowRet | 16920.3253 | lb/hr
Tadp | 47 | °F | QairSup | 3756.0909 | cfm
BPFactor | 0.1 |  | QAairSup | 3760.0723 | scfm
QSairRet | 3760.0723 | scfm
|  |  | TdbSup | 50.28 | °F
TdbRet | 79.8 | °F | TwbSup | 49.48 | °F
TwbRet | 67.1 | °F | HRatioadp | 0.0069743 | lbw/lba
Elev | 0 | ft.
AtmPress | 14.696 | psia | qTotal | 199.3319 | MBtu/h
APinHg | 29.2252 | in Hg | qSensible | 122.4573 | MBtu/h
|  |  | SHRcoil | 0.61434
HRatioRet | 0.011634 | lbw/lba | HRatioSup | 0.0074403 | lbw/lba
| 81.439 | Grains |  | 52.0819 | Grains
RelHumRet | 52.2899 | % | RelHumSup | 94.7779 | %
SpHtRet | 0.24517 | Btu/lb-°F | SpHtSup | 0.2433 | Btu/lb-°F
EnalRet | 31.908 | Btu/lb | EnalSup | 20.1274 | Btu/lb
SpVolRet | 14.1841 | cu.ft./lb | SpVolSup | 13.3192 | cu.ft./lb
DewPtRet | 60.8329 | °F | DewPtSup | 48.7626 | °F
T(dbRet) T(wbRet)
T(dbSup) T(wbSup)
T(adp)
Q(airRet)
Q(airSup)
BPFactor = 1-(TdbRet-TdbSup)/(TdbRet-Tadp)
t(ret)
t(sup)
t(adp)